## Specification
|  | Issue: | A |  | Origination Date: | 2019-12-04
|  | File Ref: | 1.0 |  | Author: | P Kelly
|  | Project #: | 361 |  | Last Update:
|  | Assembly: | 04255ASSM |  | Updated by:
Test # | Test Decription | Supply Voltage | Voltage Tolerance | Applied Fault | Fault Tolerance | Pass Criteria |  | Unit
[6 empty] | Min | Max
1 | Test PMR Mosfet OFF | 0V | 0Vac | N/A | N/A | 320 | 330 | mVdc
2 | Measure Module current consumption - From AC Voltage source. (Current consumption measurement across a resistor) | 48V L1 - N | +2Vac | N/A | N/A | 75 | 150 | mVac
3 | Test PMR Mosfet ON | 48V L1 - N | +2Vac | N/A | N/A | 200 | 600 | mVdc
4 | Measure Module current consumption - From AC Voltage source. (Current consumption measurement across a resistor) | 268V L1 - N | +2Vac | N/A | N/A | 75 | 130 | mVac
5 | Measure Module current consumption - From AC Voltage source. (Current consumption measurement across a resistor) | 268V L2 - N | +2Vac | N/A | N/A | 75 | 130 | mVac
6 | Measure Module current consumption - From AC Voltage source. (Current consumption measurement across a resistor) | 268V L3 - N | +2Vac | N/A | N/A | 75 | 130 | mVac
7 | Measure Module current consumption - From AC Voltage source. (Current consumption measurement across a resistor) | 230V 3φ | +2Vac | N/A | N/A | 65 | 90 | mVac
8 | Measure 50Hz TRIP Time - IΔn | 48V L1 - N | +2Vac | 29.9mA | -0.2mA | 130 | 220 | ms
9 | Measure 135° Pulsating DC Upper Level | 48V L1 - N | +2Vac | 36mA | ±0.5mA | TRIP |  | N/A
10 | Measure 50Hz TRIP Time - 7IΔn Half Wave Start Angle 0° | 48V L1 - N | +2Vac | 210mA | -2mA | 10 | 36 | ms
11 | Measure DC TRIP Time - 10A DC Any polarity | 48V L1 - N | +2Vac | 10A | -0.5A | 10 | 25 | ms
12 | Measure 50Hz Lower Level | 48V L1 - N | +2Vac | 18mA | ±0.2mA | NO TRIP |  | N/A
13 | Measure 50Hz Upper Level | 48V L1 - N | +2Vac | 23mA | ±0.2mA | TRIP |  | N/A
14 | Measure DC Lower Level - DC I | 48V L1 - N | +2Vac | 29mA | ±0.2mA | NO TRIP |  | N/A
15 | Measure DC Upper Level - DC I | 48V L1 - N | +2Vac | 34mA | ±0.2mA | TRIP |  | N/A
16 | Measure DC Lower Level - DC II | 48V L1 - N | +2Vac | -29mA | ±0.2mA | NO TRIP |  | N/A
17 | Measure DC Upper Level - DC II | 48V L1 - N | +2Vac | -34mA | ±0.2mA | TRIP |  | N/A
18 | Measure DC TRIP Time - 10IΔn DC | 48V L1 - N | +2Vac | 300mA | ±2mA | 10 | 20 | ms
19 | Measure 1kHz TRIP Time - 14IΔn | 268V 3φ | +2Vac | 420mA | -5mA | 80 | 230 | ms
20 | Inrush Test - 11IΔn - Apply one full half cycle, start angle 0° | 268V 3φ | +2Vac | 310mA | ±5mA | NO TRIP |  | N/A
21 | Test PMR Mosfet OFF | 0V | 0Vac | N/A | N/A | 320 | 330 | mVdc
22 | [7 empty] | _ _
23 | [7 empty] | _ _
24 | [7 empty] | _ _
25 | [7 empty] | _ _
26 | [7 empty] | _ _
27 | [7 empty] | _ _
28 | [7 empty] | _ _
29 | [7 empty] | _ _
30 | [7 empty] | _ _
Document Revision History
|  | ECR | Rev | Date | Description |  | Author | Approved By