## Specification
Issue: | A |  | Origination Date: | 2019-11-18
File Ref: | 1.0 |  | Author: | P Kelly
Project #: | 361 |  | Last Update:
Assembly: | 04257ASSM |  | Updated by:
Test # | Test Decription | Supply Voltage | Voltage Tolerance | Applied Fault |  | Pass Criteria |  | Unit
[6 empty] | Min | Max
1 | Test PMR Mosfet OFF | 0V | 0Vac | N/A | N/A | 320 | 330 | mvdc
2 | Measure Module current consumption - From AC Voltage source. (Current consumption measurement across a resistor) | 48V L1 - N | +2Vac | N/A | N/A | 75 | 150 | mvac
3 | Test PMR Mosfet ON | 48V L1 - N | +2Vac | N/A | N/A | 200 | 600 | mvdc
4 | Measure Module current consumption - From AC Voltage source. (Current consumption measurement across a resistor) | 268V L1 - N | +2Vac | N/A | N/A | 75 | 130 | mvac
5 | Measure Module current consumption - From AC Voltage source. (Current consumption measurement across a resistor) | 268V L2 - N | +2Vac | N/A | N/A | 75 | 130 | mvac
6 | Measure Module current consumption - From AC Voltage source. (Current consumption measurement across a resistor) | 268V L3 - N | +2Vac | N/A | N/A | 75 | 130 | mvac
7 | Measure Module current consumption - From AC Voltage source. (Current consumption measurement across a resistor) | 230V 3φ | +2Vac | N/A | N/A | 75 | 90 | mvac
8 | Measure 50Hz TRIP Time - IΔn | 48V L1 - N | +2Vac | 299mA | -2mA | 140 | 240 | ms
9 | Measure 135° Pulsating DC Upper Level | 48V L1 - N | +2Vac | 360mA | ±5mA | TRIP |  | N/A
10 | Measure 50Hz TRIP Time - 7IΔn Half Wave Start Angle 0° | 48V L1 - N | +2Vac | 2.1A | -20mA | 10 | 36 | ms
11 | Measure DC TRIP Time - 10A DC Any polarity | 48V L1 - N | +2Vac | 10A | -0.5A | 10 | 25 | ms
12 | Measure 50Hz Lower Level | 48V L1 - N | +2Vac | 200mA | ±2mA | NO TRIP |  | N/A
13 | Measure 50Hz Upper Level | 48V L1 - N | +2Vac | 250mA | ±2mA | TRIP |  | N/A
14 | Measure DC Lower Level - DC I | 48V L1 - N | +2Vac | 190mA | ±2mA | NO TRIP |  | N/A
15 | Measure DC Upper Level - DC I | 48V L1 - N | +2Vac | 250mA | ±2mA | TRIP |  | N/A
16 | Measure DC Lower Level - DC II | 48V L1 - N | +2Vac | -190mA | ±2mA | NO TRIP |  | N/A
17 | Measure DC Upper Level - DC II | 48V L1 - N | +2Vac | -250mA | ±2mA | TRIP |  | N/A
18 | Measure DC TRIP Time - 10IΔn DC | 48V L1 - N | +2Vac | 3.0A | -20mA | 10 | 25 | ms
19 | Measure 1kHz TRIP Time - 14IΔn | 268V 3φ | +2Vac | 4.2A | -50mA | 18 | 50 | ms
20 | Inrush Test - 11IΔn - Apply one full half cycle, start angle 0° | 268V 3φ | +2Vac | 3.2A | -50mA | NO TRIP |  | N/A
21 | Test PMR Mosfet OFF | 0V | 0Vac | N/A | N/A | 320 | 330 | mvdc