## Specification
|  | Issue: | A |  | Origination Date: | 2019-12-04
|  | File Ref: | 1.0 |  | Author: | P Kelly
|  | Project #: | 479 |  | Last Update:
|  | Assembly: | 04987ASSM |  | Updated by:
Test # | Test Decription | Supply Voltage | Voltage Tolerance | Applied Fault | Fault Tolerance | Pass Criteria |  | Unit
[6 empty] | Min | Max
1 | Test PMR Mosfet OFF | 0V | 0Vac | N/A | N/A | 320 | 330 | mVdc
2 | Measure Module current consumption - From AC Voltage source. (Current consumption measurement across a resistor) | 48V L1 - N | +2Vac | N/A | N/A | 75 | 130 | mVac
3 | PSU Voltage - Stage 2 | 48V L1 - N | +2Vac | N/A | N/A | 14.5 | 15.5 | Vdc
4 | Test PMR Mosfet ON | 48V L1 - N | +2Vac | N/A | N/A | 200 | 600 | mVdc
5 | Test LED Voltage | 48V L1 - N | +2Vac | N/A | N/A | 6.5 | 10.5 | Vdc
6 | PSU Voltage - Stage 2 | 55V L1 - N | ±2 Vac | N/A | N/A | 14.5 | 15.5 | Vdc
7 | PSU Voltage - Stage 1 | 55V L1 - N | +2Vac | N/A | N/A | 18.5 | 20.5 | Vdc
8 | Measure Module current consumption - From AC Voltage source. (Current consumption measurement across a resistor) | 268V L1 - N | +2Vac | N/A | N/A | 75 | 120 | mVac
9 | Measure Module current consumption - From AC Voltage source. (Current consumption measurement across a resistor) | 268V L2 - N | +2Vac | N/A | N/A | 75 | 120 | mVac
10 | Measure Module current consumption - From AC Voltage source. (Current consumption measurement across a resistor) | 268V L3 - N | +2Vac | N/A | N/A | 75 | 120 | mVac
11 | Measure Module current consumption - From AC Voltage source. (Current consumption measurement across a resistor) | 230V 3φ | +2Vac | N/A | N/A | 75 | 120 | mVac
12 | Measure 50Hz TRIP Time - IΔn | 48V L1 - N | +2Vac | 299mA | -2mA | 100 | 180 | ms
13 | Measure 135° Pulsating DC Upper Level | 48V L1 - N | +2Vac | 420mA | -5mA | TRIP |  | N/A
14 | Measure 50Hz TRIP Time - 7IΔn Half Wave Start Angle 0° | 48V L1 - N | +2Vac | 2.1A | -20mA | 15 | 28 | ms
15 | Measure DC TRIP Time - 10A DC Any polarity | 48V L1 - N | +2Vac | 10A | -0.5A | 8 | 25 | ms
16 | Measure 50Hz Lower Level | 48V L1 - N | +2Vac | 205mA | ±2mA | NO TRIP |  | N/A
17 | Measure 50Hz Upper Level | 48V L1 - N | +2Vac | 250mA | ±2mA | TRIP |  | N/A
18 | Measure DC Lower Level - DC I | 48V L1 - N | +2Vac | 180mA | ±2mA | NO TRIP |  | N/A
19 | Measure DC Upper Level - DC I | 48V L1 - N | +2Vac | 220mA | ±2mA | TRIP |  | N/A
20 | Measure DC Lower Level - DC II | 48V L1 - N | +2Vac | -180mA | ±2mA | NO TRIP |  | N/A
21 | Measure DC Upper Level - DC II | 48V L1 - N | +2Vac | -220mA | ±2mA | TRIP |  | N/A
22 | Measure DC TRIP Time - 10IΔn DC | 48V L1 - N | +2Vac | 3.0A | -20mA | 10 | 22 | ms
23 | Measure 1kHz TRIP Time - 14IΔn | 268V 3φ | +2Vac | 4.2A | -50mA | 20 | 50 | ms
24 | Inrush Test - 11IΔn - Apply one full half cycle, start angle 0° | 268V 3φ | +2Vac | 3.4A | -50mA | NO TRIP |  | N/A
25 | Test PMR Mosfet OFF | 0V | 0Vac | N/A | N/A | 320 | 330 | mVdc
26 | [7 empty] | _ _
27 | [7 empty] | _ _
28 | [7 empty] | _ _
29 | [7 empty] | _ _
30 | [7 empty] | _ _
Document Revision History
|  | ECR | Rev | Date | Description |  | Author | Approved By