## Specification
|  | Issue: | A |  | Origination Date: | 2019-11-28
|  | File Ref: | 1.0 |  | Author: | P Kelly
|  | Project #: | 443 |  | Last Update:
|  | Assembly: | RCM14-01 |  | Updated by:
Test # | Test Decription | Supply Voltage | Voltage Tolerance | Applied Fault | Fault Tolerance | Pass Criteria |  | Unit
[6 empty] | Min | Max
1 | Check Response Light and Out | 13.5V | ±0.1V | N/A | N/A | Response Light and Output Turns Off |  | N/A
2 | Measure Module current consumption | 13.5V | ±0.1V | N/A | N/A | 1 | 5 | mAdc
3 | Apply Lower Level DC I | 13.5V | ±0.1V | 3.2mA | ±0.05mA | NO TRIP |  | N/A
4 | Increment Fault Current to Upper Level DC I or until Device Trips (Fault Current Level to be applied for sufficient time to allow device respond - e.g. 1mA/second LL DC I and UL DC I Applied for 1 sec) | 13.5V | ±0.1V | 5.8mA | ±0.05mA | TRIP |  | mAdc
5 | Measure Trip Time at IΔn DC I | 10.7V | ±0.1V | 6mA | -0.1mA | 0 | 800 | ms
6 | Apply Lower Level DC II | 13.5V | ±0.1V | 3.2mA | ±0.05mA | NO TRIP |  | N/A
7 | Increment Fault Current to Upper Level DC II or until Device Trips (Fault Current Level to be applied for sufficient time to allow device respond - e.g. 1mA/second LL DC II and UL DC II Applied for 1 sec) | 13.5V | ±0.1V | 5.8mA | ±0.05mA | TRIP |  | mAdc
8 | Measure Trip Time at IΔn DC II | 10.7V | ±0.1V | 6mA | -0.1mA | 0 | 800 | ms
9 | Test Winding. Apply Supply Voltage to Test Input | 10.7 | ±0.1V | N/A | N/A | TRIP |  | N/A
10 | Measure Trip Time at 10IΔn DC I | 10.7V | ±0.1V | 60mA | -1mA | 0 | 130 | ms
11 | Measure Trip Time at 10IΔn DC II | 10.7V | ±0.1V | 60mA | -1mA | 0 | 130 | ms
12 | Apply 50Hz AC Fault | 10.7V | ±0.1V | 100mA | ±1mA | NO TRIP |  | N/A
13 | Green LED Check | 10.7V | ±0.1V | N/A | N/A | 100 | 1000 | mVdc
14 | Red LED Check | 10.7V | ±0.1V | N/A | N/A | 100 | 1000 | mVdc
15 | [7 empty] | _ _
16 | [7 empty] | _ _
17 | [7 empty] | _ _
18 | [7 empty] | _ _
19 | [7 empty] | _ _
20 | [7 empty] | _ _
21 | [7 empty] | _ _
22 | [7 empty] | _ _
23 | [7 empty] | _ _
24 | [7 empty] | _ _
25 | [7 empty] | _ _
26 | [7 empty] | _ _
27 | [7 empty] | _ _
28 | [7 empty] | _ _
29 | [7 empty] | _ _
30 | [7 empty] | _ _
Document Revision History
|  | ECR | Rev | Date | Description |  | Author | Approved By