## Specification
Issue: | B |  | Origination Date: | 2019-03-04
File Ref: | 1.1 |  | Author: | P Kelly
Project #: | 479 |  | Last Update:
Assembly: | 04851ASSM |  | Updated by:
Test # | Test Decription | Supply Voltage | Voltage Tolerance | Applied Fault |  | Pass Criteria |  | Unit
[6 empty] | Min | Max
1 | Test PMR Mosfet OFF | 0V | 0Vac | N/A | N/A | 320 | 330 | mvdc
2 | Measure Module current consumption - From AC Voltage source. (Current consumption measurement across a resistor) | 48V L1 - N | +2Vac | N/A | N/A | 75 | 130 | mvac
3 | PSU Voltage - Stage 2 | 48V L1 - N | +2Vac | N/A | N/A | 14.5 | 15.5 | vdc
4 | Test PMR Mosfet ON | 48V L1 - N |  | N/A | N/A | 200 | 600 | mvdc
5 | Power on LED response | 13.5V |  | N/A | N/A | 100 | 1000 | mvdc
6 | Fault ON LED response | 13.5V |  |  |  | 100 | 1000 | mvdc
7 | PSU Voltage - Stage 2 | 55V L1 - N | ±2 Vac | N/A | N/A | 14.5 | 15.5 | vdc
8 | PSU Voltage - Stage 1 | 55V L1 - N | +2Vac | N/A | N/A | 18.5 | 20.5 | vdc
9 | Measure Module current consumption - From AC Voltage source. (Current consumption measurement across a resistor) | 268V L1 - N | +2Vac | N/A | N/A | 75 | 120 | mvac
10 | Measure Module current consumption - From AC Voltage source. (Current consumption measurement across a resistor) | 268V L2 - N | +2Vac | N/A | N/A | 75 | 120 | mvac
11 | Measure Module current consumption - From AC Voltage source. (Current consumption measurement across a resistor) | 268V L3 - N | +2Vac | N/A | N/A | 75 | 120 | mvac
12 | Measure Module current consumption - From AC Voltage source. (Current consumption measurement across a resistor) | 230V 3φ | +2Vac | N/A | N/A | 75 | 120 | mvac
13 | Measure 50Hz TRIP Time - IΔn | 48V L1 - N | +2Vac | 29.9mA | -0.2mA | 110 | 180 | ms
14 | Measure 135° Pulsating DC Upper Level | 48V L1 - N | +2Vac | 36mA | ±0.5mA | TRIP |  | N/A
15 | Measure 50Hz TRIP Time - 7IΔn Half Wave Start Angle 0° | 48V L1 - N | +2Vac | 210mA | -2mA | 18 | 35 | ms
16 | Measure DC TRIP Time - 10A DC Any polarity | 48V L1 - N | +2Vac | 10A | -0.5A | 8 | 25 | ms
17 | Measure 50Hz Lower Level | 48V L1 - N | +2Vac | 20.5mA | ±0.2mA | NO TRIP |  | N/A
18 | Measure 50Hz Upper Level | 48V L1 - N | +2Vac | 24mA | ±0.2mA | TRIP |  | N/A
19 | Measure DC Lower Level - DC I | 48V L1 - N | +2Vac | 30mA | ±0.2mA | NO TRIP |  | N/A
20 | Measure DC Upper Level - DC I | 48V L1 - N | +2Vac | 35mA | ±0.2mA | TRIP |  | N/A
21 | Measure DC Lower Level - DC II | 48V L1 - N | +2Vac | -30mA | ±0.2mA | NO TRIP |  | N/A
22 | Measure DC Upper Level - DC II | 48V L1 - N | +2Vac | -35mA | ±0.2mA | TRIP |  | N/A
23 | Measure DC TRIP Time - 10IΔn DC | 48V L1 - N | +2Vac | 300mA | ±2mA | 10 | 20 | ms
24 | Measure 1kHz TRIP Time - 14IΔn | 268V 3φ | +2Vac | 420mA | -5mA | 105 | 230 | ms
25 | Inrush Test - 11IΔn - Apply one full half cycle, start angle 0° | 268V 3φ | +2Vac | 330mA | +10mA | NO TRIP |  | N/A
26 | Test PMR Mosfet OFF | 0V | 0Vac | N/A | N/A | 320 | 330 | mvdc